## Inspection notification
INSPECTION NOTIFICATION |  |  |  | Back
Applicant expected to have completed DM/Trakhees inspection prior to this
Ref
| 1 | Solar NOC Reference
| 2 | Point of Connection (LV or MV)
| 3 | Inspection readiness date (mm/dd/yyyy)
| Ref |  | Uploaded? (Y/N)
| 1 | Site setting out plan
| 2 | As built drawings
| 3 | Solar equipment details (solar module, inverter, interface protection, cables, switchyard etc)
| 4 | Dubai Municipality approved affection Plan/other utilities affection plan
| 5 | Building Completion Certificate from Dubai Municipality
| 6 | Owner’s Passport copy/Trade License copy
| 7 | Authorization letter from the owner to his representative
| 8 | A copy of DEWA approved Design and Shop Drawings
| 9 | A copy of DEWA approved Connected Load/Max
| 10 | Captive load Demand Details
| 11 | Owner’s NOC (if tenant application)
| 12 | Building NOC (6 month validity from the date of issue)
| 13 | For MV connections with private substations, the following additional information is required:
| 13.1 | Single line diagram with details on metering and protection system
| 13.2 | Undertaking letter stating that the load on each feeder shall not exceed 3MW (175A) in normal operation and 6MW (350A) in case of contingency if the adjacent feeder fails
| 13.3 | Report of "Real measurement of harmonics" after full commissioning of the equipment.
| 13.4 | Step by step relay setting calculations.
| 13.5 | Owner’s undertaking stating “Our equipment are suitable to energize in line with DEWA network system“ and confirm that the protection relays are set as per DEWA approved setting.
| 13.6 | HV cable Jointer’s list in details (approved by DEWA);
| 13.7 | Names and telephone numbers of contact person for the project who should be available to contact on a 24 hour basis;
| 13.8 | Name of technical staff, competent in the switchgear operation and issuing of permit stating that cable is safe for work, and also ensure no one, will operate during test & repairing time.
| 13.9 | Factory & Site test report for the transformer/breaker, MV cable, etc. and test result for the transformer inrush unbalance current to be forwarded for verification;
| 13.1 | Operation philosophy (interlocking details) - to be incorporated in the single line diagram
| 13.11 | All catalogues for CT, VT, relay & motor.
Other document to be uploaded after completion of first inspection
| 1 | Technical Dossier document (for all PV projects - to be submitted after Electrical inspection)
| 2 | Performance detail document ( for projects >=100kW, to be submitted after Energy meter installation)